## Slide 1
EnviSense Temp. + Humidity Sensor
Wall/Duct Mount Temp + Humidity Sensors
Input Power | 24vDC (18vDC to 30vDC)
Analog Output | 4 to 20 mA, 0 to 10 V (Factory Default)
Operating Temperature Range | -30°C to 70°C (-20 to 158 °F) without display Model
Operating Humidity Range | 0 to 95% RH non-condensing
Housing Material | ABS plastic
IP Rating | IP 65 for Cabinet, IP54 for Sensor Nozzle
Sensor Type | Capacitive Humidity sensor (Digital)
Accuracy | Option1: ±2% RH (For range of 10-90%RH) Option1: ±3% RH (For range of 20-80%RH)
Hysteresis | 1.5% typical
Stability | <+/-1% @ 20°C (68 °F) annually
Output Range | 0 to 100% RH
Resolution | 0.1% RH
Sensor Type | Band Gap Temperature (Digital)
Accuracy | Option1: ±0.2°C (For the range of 0°C to 60°C) Option1: ±0.3°C (For the range of 0°C to 40°C)
Resolution | 0.1°C (0.1°F)
Range | 0 to 70°C (32 to 158°F)
RH TRANSMITTER
TEMPERATURE TRANSMITTER
Terminal Blocks | Screw terminals, 18-24 AWG
WIRING TERMINALS
WARRANTY
Limited Warranty
1 year
enviSENSE series devices are high performance, “all-in-one” temperature and Humidity transmitter. Its high reliability industrial design and offers 4-20 mA output signal transmission. It is wired loop transmitter (Two wire transmitter) It accurately measures humidity using capacitive sensor technology & temperature using band gap sensor technology. Wall mount, duct mount versions available.
Technical Specification
COMPLIANCE INFORMATION
Agency Approval | CE Compliance Design
enviSENSE Series
Digital Sensor with capacitive sensor technology for Rh & band gap sensor technology, Factory Calibrated.
IP65 Cabinet & IP54 Sensor Nozzle
Long Term Stability for T+RH sensor
High Performance digital sensors allows accurate measurement & fast Response of 10ms
Sensor Element
Accurate Measurement
Stability
Weather Proof
Easy to Install
Accuracy Chart
Version: V1.3_17112023
Field Calibration | Available (Need to use external probe and Calibration Software Utility)

## Slide 2
Dimensional Drawing
Ordering Information
Humidity
CH-1
CH-2
GND
24V
Temp
GND
24V
D-7/Unit No 254, Bhumi World Industrial Park, Pimplas, Bhiwandi, Thane, Maharashtra - 421302. INDIA
Boardline - +91-8767-247-247 | Email: presales@enviroworld.in Web: www.enviro-technologies.com
ENVIRO TECHNOLOGIES
Temp + RH Transmitter Wall & Duct Mount (No Display)
Wiring Diagram
EnviSense Temp. + Humidity Sensor
Note: Product images are for illustrative purpose only and may differ from the actual product. All Specs are subject to change without notice due to continuous improvements
Sensor Type
Output
Display Type
Accuracy
K01 = Temperature
K02 + RH
K03 = Temp + RH
1 = 4 - 20 mA
2 = 0 - 10 V
3 = RS485 MODBUS
0 = No Display
2 = LCD TFT Display
1 = Temp: ± 0.3 Degree; ± 3% RH
2 =Temp: ± 0.2 Degree; ± 2% RH
Enclosure
1 = ABS
2 = Flameproof
3 =Front SS Plate with Back MS Box
Mounting
1 = Wall Mount
2 = Duct Mount
Example:
K03
0
1
2
1
1
ETT
ETT
1
2
3
4
5
6
1
2
3
4
5
6
Description : enviSENSE - Sensor type: Temperature + Humidity, Display Type: No Display, Output: 4 - 20 mA, Accuracy: Temp: ± 0.2 Degree ; ± 2% RH, Mounting: Wall Mount, Enclosure: ABS
Model No : ETT-K03-012-11